## Sheet1 (hidden)
01301100 | 10301100 | 0 | 0001 | 0011 | 0000 | 0001 | 0001 | 0000 | 0000
01301D00 | 10301D00 | 0 | 0001 | 0011 | 0000 | 0001 | 1101 | 0000 | 0000
01901100 | 10901100 | 0 | 0001 | 1001 | 0000 | 0001 | 0001 | 0000 | 0000
|  |  |  | 0101 | 0000
01901200 | 10901200 | 0 | 0001 | 1001 | 0000 | 0001 | 0010 | 0000 | 0000
|  |  |  | 0101 | 0000
0D202100 | 1C202100 | 0 | 1101 | 0010 | 0000 | 0010 | 0001 | 0000 | 0000
0D202F00 | 1C202F00 | 0 | 1101 | 0010 | 0000 | 0010 | 1111 | 0000 | 0000
0D203100 | 1C203100 | 0 | 1101 | 0010 | 0000 | 0011 | 0001 | 0000 | 0000
11204100 | 10204100 | 1 | 0001 | 0010 | 0000 | 0100 | 0001 | 0000 | 0000
11204F00 | 10204F00 | 1 | 0001 | 0010 | 0000 | 0100 | 1111 | 0000 | 0000
| 5 |  |  |  | 0000 | 0101
15208100 | 14208100 | 1 | 0101 | 0010 | 0000 | 1000 | 0001 | 0000 | 0000
| 9 |  |  |  | 0000 | 1001
15208F00 | 14208F00 | 1 | 0101 | 0010 | 0000 | 1000 | 1111 | 0000 | 0000
0001
0011
0CF20101 | 1CF20101 | 0 | 1100 | 1111 | 0010 | 0000 | 0001 | 0000 | 0001
0CF20201 | 1CF20201 | 0 | 1100 | 1111 | 0010 | 0000 | 0010 | 0000 | 0001
待屏蔽 | B |  |  | 0111
080a0aff | 180a0aff | 0 | 1000 | 0000 | 1010 | 0000 | 1010 | 1111 | 1111
080a0bff | 180a0bff | 0 | 1000 | 0000 | 1010 | 0000 | 1011 | 1111 | 1111
080a05ff | 180a05ff | 0 | 1000 | 0000 | 1010 | 0000 | 0101 | 1111 | 1111
0CF20301 | 1CF20301 | 0 | 1100 | 1111 | 0010 | 0000 | 0011 | 0000 | 0001
0CF20401 | 1CF20401 | 0 | 1100 | 1111 | 0010 | 0000 | 0100 | 0000 | 0001
08f50A01 | 18f50A01 | 0 | 1000 | 1111 | 0101 | 0000 | 1010 | 0000 | 0001
04F10B00 | 14F10B00 | 0 | 0100 | 1111 | 0001 | 0000 | 1011 | 0000 | 0000
0CF20801 | 1CF20801 | 0 | 1100 | 1111 | 0010 | 0000 | 1000 | 0000 | 0001
08f50B01 | 18f50B01 | 0 | 1000 | 1111 | 0101 | 0000 | 1011 | 0000 | 0001
04F10C00 | 14F10C00 | 0 | 0100 | 1111 | 0001 | 0000 | 1100 | 0000 | 0000
0CF20901 | 1CF20901 | 0 | 1100 | 1111 | 0010 | 0000 | 1001 | 0000 | 0001
| D | 9 | F | F | 1101 | F | F | F | F | 0x9FFDFFFF
|  | 9 | F | F | D | 3 | F | F | F | 0x9FFD3FFF
|  | 9 | F | F | D | 0 | F | F | F | 0x9FFD1FFF
|  | 9 | F | F | F | 9 | F | 0 | F | 0x9FDF9FFF
|  | 9 | F | F | F | F | 3 | F | F | 0x9FFFF3FF
| 00301100 | 0000 | 0001 | 0001 | 1010
| 00301D00 | 0000 | 0001 | 1101
| 00901100 | 0000 | 0001 | 0001 | [8 empty] | 00301100 |  | 00301100
| 00901200 | 0000 | 0001 | 0010 | [8 empty] | 00301D00 |  | 00301D00
| 0C202100 | 0000 | 0010 | 0001 | [8 empty] | 00901100 | 00901100 | 00901100
| 0C202F00 | 0000 | 0010 | 1111
| 0C203100 | 0000 | 0011 | 0001 | [8 empty] | 00901200 | 00901200 | 00901200
| 10204100 | 0000 | 0100 | 0001 | [7 empty] | 00301100
| 10204F00 | 0000 | 0100 | 1111 | [7 empty] | 00301D00 | 0C202100 |  | 0C202100
| 14208100 | 0000 | 1000 | 0001 | [7 empty] | 00901100 | 0C202F00 |  | 0C202F00
| 14208F00 | 0000 | 1000 | 1111 | [7 empty] | 00901200 | 0C203100 |  | 0C203100
| ##DFF## | [9 empty] | 0x9FFD0FFF | 0x9FFD1FFF | 0x9FFD3FFF | 0x9FDF9FFF
| 08f50A01 | 0101 | 0000 | 1010 | [6 empty] | 08f50A01 | 08f50A01 | 08f50A01 | 080a0aff | 08f50A01
| 04F10B00 | 0001 | 0000 | 1011 | [6 empty] | 04F10B00 | 04F10B00 | 04F10B00 | 080a0bff | 04F10B00
| 08f50B01 | 0101 | 0000 | 1011 | [6 empty] | 08f50B01 | 08f50B01 | 08f50B01 | 080a05ff | 08f50B01
| 04F10C00 | 0001 | 0000 | 1100 | [6 empty] | 04F10C00 | 04F10C00 | 04F10C00 |  | 04F10C00
| ##9FF## | 1001
| ##2FF## | 10
| ##AFF## | 1010
0x9FFFF3FF

## Charger ModbusRtu (ID == 1)
Register Address（decimalism） | Register Type | Register Name |  | Effective Range | note
Charger Control Message
10000 | RO | The type of machine High | PC
10001 | RO | The type of machine Low | 1800
10002 | WR | Serial number High
10003 | WR | Serial number Low
10004 | RO | Hardware version | 1.0.00
10005 | RO | Software version | 1.0.00
10006 | WR | PV voltage calibration coefficient | 16384
10007 | WR | Battery voltage calibration coefficient | 16384
10008 | WR | Charger current calibration coefficient | 16384
10009 | RO | Rated Current | 0.1A
10010 | RO | Communication Protocol Edition | 1.04.14
10011-10100 | WR | reserved | reserved
10101 | WR | charger work enable | 0:OFF 1:ON | effective range：0,1 the default value is 1；
10002 | WR | reserved | reserved
10103 | WR | Battery Float voltage | 0.1V | 48V:480-640(48.0-64.0)V the default value is 54.0V 24V:240-320(24.0-32.0)V the default value is 27.0V 12V:120-160(12.0-16.0)V the default value is 13.5V
10104 | WR | Battery Absorption voltage | 0.1V | 48V:480-64.0(48.0-64.0)V the default value is 56.4V 24V:240-32.0(24.0-32.0)V the default value is 28.2V 12V:120-16.0(24.0-16.0)V the default value is 14.1V
10105 | WR | Battery low voltage | 0.1V | 48V:340-440(34.0-44.0)V the default value is 34.0V 24V:170-220(17.0-22.0)V the default value is 17.0V 12V:85-110(8.5-11.0)V the default value is 8.5V
10106 | WR | reserved
10107 | WR | reserved
10108 | WR | Max charger current | 0.1A | 0.1A effective range：(0.1-80.0)A
10109 | WR | reserved
10110 | WR | Battery type | 0:no choose 1:Use defined battery 2:lithium battery 3:SEALED_LEAD battery 4:AGM battery 5:GEL battery 6:FLOODED battery | the default value is 4 ；effective range：0,6 | Refer to the frame Charging point
10111 | WR | Battery AH | 1AH | effective range:(0-900)AH the default value is 100AH
10112 | WR | Remove the accumulated data | 0:No remove the accumulated data 1:Remove the accumulated data | the default value is 0；effective range：0,1
10113 | WR | Battery Voltage Grade | 0:aotumatically detected 12:12V 24:24V 36:36V 48:48V
10114 | WR | reserved
10115 | WR | reserved
10116 | WR | CV charing Max time | 1min | 5~900(5-900)min the default value is 150min
10117 | WR | BTS temperature compensation ratio | 0.1mV | 0~600(0-60.0)mV the default value is 0.0mV
10118 | WR | Battery equalization enable | 0:Disable 1:Enable | effective range：0,1 the default value is 0；
10119 | WR | Battery Equalization voltage | 0.1V | 48V:480-640(48.0-64.0)V the default value is 58.4V 24V:240-320(24.0-32.0)V the default value is 29.2V 12V:120-160(12.0-16.0)V the default value is 14.6V
10120 | WR | The Max Current of battery equalization | 0.1A | 0.1A 1-800 effective range：(0.1-80.0)A
10121 | WR | Battery equalized time | 1min | 5-900(5-900)min the default value is 150min
10122 | WR | Battery Equalized timeout | 1min | 5-900(5-900)min the default value is 150min
10123 | WR | Equalization interval | 1day | 0-90(0-90)day the default value is 30 days
10124 | WR | Equalization actived immediately | 0:No effect 1:Action | the default value is 0; effective range:0,1
10125 | WR | System setting |  | refer to the frame System setting bit
10126 | WR | Reset the parameter | 0:No effect 1:Action | the default value is 0; effective range:0,1
16001 | WR | customiz combine charger with Utility current setting | 0.1A | for customize when the baudrate is 2400,you maybe use it. 0.1A 1-1400 effective range：(0.1-140.0)A
16002 | WR | customize start machine setting | 0:No effect 1:Action | for customize when the baudrate is 2400,you must write 1 if you want start the machine
Register Address（decimalism） | Register Type | Register Name | Physical Unit | Effective Range | note
Charger Display Message
15201 | RO | Charger workstate | 0: Initialization Mode 1: Selftest Mode 2: Work Mode 3: Stop Mode
15202 | RO | Mppt state | 0: Stop 1: MPPT 2: Current limiting
15203 | RO | charging state | 0: Stop 1: Absorb charge 2: Float charge 3: EQ charge
15204 | RO | reserved
15205 | RO | PV voltage | 0.1V | (0.0-150.0)V
15206 | RO | Battery voltage | 0.1V | (0.0-80.0)V
15207 | RO | Charger current | 0.1A | (0.0-90.0)A
15208 | RO | Charger power | 1W | (0-5000)W
15209 | RO | Radiator temperature | 1℃ | (-40-150)℃
15210 | RO | External temperature | 1℃ | (-40-150)℃
15211 | RO | Battery Relay |  | 0: Disconnect 1:Connect
15212 | RO | PV Relay |  | 0: Disconnect 1:Connect
15213 | RO | Error message | Refer to frame Charger Error message 1
15214 | RO | Warning message | Refer to frame Charger Warning message 1
15215 | RO | BattVol Grade | 1V
15216 | RO | Rated Current | 0.1A
15217 | RO | Accumulated PV power high | 1000KWH
15218 | RO | Accumulated PV power low | 0.1KWH
15219 | RO | Accumulated day | 1day
15220 | RO | Accumulated hour | 1hour
15221 | RO | Accumulated minute | 1minute
15222 | RO | Communication Protocol Edition | 1.04.14
15223 | RO | Soc | 1%
15224 | RO | Arrow Flag | bit | Refer to the frame Arrow Flag bit
System setting bit
Bit | meaning
0 | reserved
1 | reserved
2 | reserved
3 | AutoTurnPageFlagForbid
4 | reserved
5 | reserved
6 | LcdLightEnable
7 | reserved
8 | reserved
9 | reserved
10 | reserved
11 | reserved
12 | reserved
13 | reserved
14 | reserved
15 | reserved
Arrow Flag bit
Bit |  | meaning
0 | PV-to-Machine-Arrow | 0: Disconnect 1:Connect
1 | PV_Flag | 0:Inexistence 1:Existence
2 | Machine-to-Batt-Arrow | 0: Disconnect 1:Connect
3 | Batt_Flag | 0:Inexistence 1:Existence
4 | reserved
5 | reserved
6 | reserved
7 | reserved
8 | reserved
9 | reserved
10 | reserved
11 | reserved
12 | reserved
13 | reserved
14 | reserved
15 | reserved
Charging point
Parameter | Battery type | Absorb Stage | Float Stage | Equalize Stage
Unit |  | volt | volt | volt
Default | AGM/Gel/LEAD | 57.6V/28.8V/14.4V | 54.8V/27.4V/13.7V | 58.4V/29.2V/14.6V
Option | Flooded | 56.8V/28.4V/14.2V | 54.8V/27.4V/13.7V | 58.4V/29.2V/14.6V
Option | Customized | 56.4V/28.2V/14.1V | 54.0V/27.0V/13.5V | 58.4V/29.2V/14.6V

## Charger Alarm
Charger error message 1 |  |  | Charger Warning message 1
Bit | meaning | description | Charger Warning message 1 | meaning | description
0 | Hardware protection | 0：normal 1：fault | 0 | Fan Error | 0：normal 1：fault
1 | Over current | 0：normal 1：fault | 1 | reserved | 0：normal 1：fault
2 | Current sensor error | 0：normal 1：fault | 2 | reserved | 0：normal 1：fault
3 | Over temperature | 0：normal 1：fault | 3 | reserved | 0：normal 1：fault
4 | PV voltage is too high | 0：normal 1：fault | 4 | reserved | 0：normal 1：fault
5 | PV voltage is too low | 0：normal 1：fault | 5 | reserved | 0：normal 1：fault
6 | Battery voltage is too high | 0：normal 1：fault | 6 | reserved | 0：normal 1：fault
7 | Battery voltage is too Low | 0：normal 1：fault | 7 | reserved | 0：normal 1：fault
8 | Current is uncontrollable | 0：normal 1：fault | 8 | reserved | 0：normal 1：fault
9 | Parameter error | 0：normal 1：fault | 9 | reserved | 0：normal 1：fault
10 | reserved | 0：normal 1：fault | 10 | reserved | 0：normal 1：fault
11 | reserved | 0：normal 1：fault | 11 | reserved | 0：normal 1：fault
12 | reserved | 0：normal 1：fault | 12 | reserved | 0：normal 1：fault
13 | reserved | 0：normal 1：fault | 13 | reserved | 0：normal 1：fault
14 | reserved | 0：normal 1：fault | 14 | reserved | 0：normal 1：fault
15 | reserved | 0：normal 1：fault | 15 | reserved | 0：normal 1：fault